## Sheet1
Address | Item Name | Modbus Type | Data Type | Description | Comments
40001 | FCU In | Holding Register | Real (32-bit) | Uses 40001 & 40002 | The temperature of the water entering the Fan Coil Unit (FCU) to cool or heat the air.
40003 | Condenser Out | Holding Register | Real (32-bit) | Uses 40003 & 40004 | Water leaving the condenser after picking up heat from the refrigerant
40005 | Evaporator Out | Holding Register | Real (32-bit) | Uses 40005 & 40006 | The "chilled water" leaving the chiller to provide cooling to the system
40007 |  | Holding Register | Real (32-bit) | Uses 40007 & 40008 | Water leaving the FCU after it has exchanged heat with the room air
40009 | Evaporator In | Holding Register | Real (32-bit) | Uses 40009 & 40010 | Warm water returning from the chamber back into the chiller to be cooled again
40011 | Geyser Out | Holding Register | Real (32-bit) | Uses 40011 & 40012 | The temperature of the hot water coming out of the heating unit (Geyser) for the Heating Mode
40013 | LP (in psi) | Holding Register | Real (32-bit) | Uses 40013 & 40014 | The pressure of the refrigerant at the compressor inlet(suction). Used for safety (Low-pressure trip)
40015 | HP (in psi) | Holding Register | Real (32-bit) | Uses 40015 & 40016 | The pressure of the refrigerant leaving the compressor(discharge). Used to prevent system bursts (High-pressure trip)
40017 | Water Pressure (in bar) | Holding Register | Real (32-bit) | Uses 40017 & 40018 | Monitors the pressure inside the pipes to ensure the pump is working and water is actually flowing
40019 | Condenser In | Holding Register | Real (32-bit) | Uses 40019 & 40020 | Cool water coming from the cooling tower into the condenser to absorb heat
40021 | Geyser In | Holding Register | Real (32-bit) | Uses 40021 & 40022 | The temperature of the water entering the geyser before being heated up
40023 | Air Condition Chamber Temperature | Holding Register | Real (32-bit) | Uses 40023 & 40024 | The current live temperature measured inside the air chamber unit.
40025 | cut ON temp cooler | Holding Register | Real (32-bit) | Uses 40025 & 40026 | The "Upper Limit". If the room gets hot, the cooling system turns back ON.
40027 | cut ON temp heater | Holding Register | Real (32-bit) | Uses 40027 & 40028 | The "Lower Limit". If the room gets cold, the heater turns back ON
40029 | evaop out set point | Holding Register | Real (32-bit) | Uses 40029 & 40030 | The set point of the evaporator out must be (7 deg to 12 deg) in normal
40031 | Air Chamber Set Temperature - Cooler Mode | Holding Register | Real (32-bit) | Uses 40031 & 40032 | The desired temperature the user wants to maintain in the chamber for cooling (eg. 18c to 28c)
40033 | Air Chamber Set Temperature - Heater Mode | Holding Register | Real (32-bit) | Uses 40033 & 40034 | The desired temperature the user wants to maintain in the chamber for heating (eg.35 c to 45 c)
40035 | Room Temperature | Holding Register | Real (32-bit) | Uses 40033 & 40035 | The desired temperature the user wants to maintain in the chamber for heating (eg.35 c to 45 c)
40037 | heater actuator feedback in percentage | Holding Register | Real (32-bit) | Uses 40035 & 40036 | A 0–100% value telling the PLC if the actutor is physically open or closed (this is feedback from the actuator to plc)
40039 | chilwater inlet actuator feedback in percentage | Holding Register | Real (32-bit) | Uses 40037 & 40038 | A 0–100% value telling the PLC if the actutor is physically open or closed (this is feedback from the actuator to plc)
40041 | supply actuator feedback in percentage | Holding Register | Real (32-bit) | Uses 40039 & 40040 | A 0–100% value telling the PLC if the actutor is physically open or closed (this is feedback from the actuator to plc)
40043 | return actuator feedback in percentage | Holding Register | Real (32-bit) | Uses 40041 & 40042 | A 0–100% value telling the PLC if the actutor is physically open or closed (this is feedback from the actuator to plc)
40045 | fcu bypass actuator feedback in percentage | Holding Register | Real (32-bit) | Uses 40043 & 40044 | A 0–100% value telling the PLC if the actutor is physically open or closed (this is feedback from the actuator to plc)
40047 | condenser inlet actuator feedback in percentage | Holding Register | Real (32-bit) | Uses 40045 & 40046 | A 0–100% value telling the PLC if the actutor is physically open or closed (this is feedback from the actuator to plc)
40049 | heater actuator | Holding Register | Int(16-bit) | Use 40047 | Analog output signal sent by the PLC to Open or Close the actuator
40050 | chilwater inlet actuator | Holding Register | Int(16-bit) | Use 40048 | Analog output signal sent by the PLC to Open or Close the actuator
40051 | fcu bypass actuator | Holding Register | Int(16-bit) | Use 40049 | Analog output signal sent by the PLC to Open or Close the actuator
40052 | return actuator | Holding Register | Int(16-bit) | Use 40050 | Analog output signal sent by the PLC to Open or Close the actuator
40053 | supply actuator | Holding Register | Int(16-bit) | Use 40051 | Analog output signal sent by the PLC to Open or Close the actuator
40054 | condener inlet actuator | Holding Register | Int(16-bit) | Use 40052 | Analog output signal sent by the PLC to Open or Close the actuator